На английский

Инвестиционная идея проекта (проектный сценарий) заключается в переводе большей части тепловой нагрузки с экологически неэффективных источников теплоснабжения района Ново-Ленино города Иркутска  (две электрокотельные) на угольную, но более эффективную котельную (КСПУ). Удельный расход угля на выработку 1 Гкал тепла на котельной составляет 0,199 тут. Удельные затраты топлива на выработку теплоэнергии, используя электроэнергию, выработанную в конденсационном режиме составляют 0,464 т.у.т/Гкал. Таким образом, показатели удельного расхода топлива на выработку электроэнергии в конденсационном цикле работы энергосистемы для выработки теплоэнергии электрокотельными «Бытовая» и «Ново-Ленино» по исходным условиям в 2,3 раза выше, чем показатели удельного расхода топлива на КСПУ. Реализация Проекта приводит к экономии топлива (угля) в энергосистеме, что в результате, вызывает соответственное сокращение выбросов парниковых газов и загрязняющих веществ из-за сокращения сжигания угля на ТЭЦ.

Для обеспечения достижения цели Проекта было предусмотрено:

-строительство новых теплосетей от КСПУ до электрокотельной «Бытовая»  протяженностью 3 711 м, Dу 600 мм;

-реконструкция теплосетей Ленинского района протяженностью 2743 м, Dy 500мм, 600мм, 700мм, 800мм;

-реконструкция котла № 3 на КСПУ для полной передачи нагрузки с электрокотельных.

Электрокотельные (ЭК) «Бытовая» и «Ново-Ленино» переводятся в резерв. Покрытие тепловых нагрузок после перевода электрокотельных в резерв будет обеспечиваться за счет увеличения выработки тепла на КСПУ.

На русский

As a result of Project realization KSPU takes the heat load of Novo-Lenino district from “Novo-Lenino” and “Bytovaya” EBHs that are put into reserve. For this purpose construction of new and reconstruction of existing heat supply networks has been planned. Project activities are implemented in parallel at various sites and in several stages.

The boiler-house of northern industrial block (KSPU) is a basic source of a heat supply of Northern and Northwest industrial blocks and housing development of Novo-Lenino district. The total heat capacity of KSPU is 257 Gcal/h, but available heat capacity is 185,4 Gcal/h. The Project activities at KSPU include major overhaul of the boiler № 3 that will help improve its capacity up to 257 Gcal/h. Installed equipment of KSPU include 5 BKZ-75-39fb boilers (put in operation in 1974-1983). Fuel is Azejsky brown coal. The design temperature schedule of a boiler-house is 150-70 °С. Before Project realisation the temperature schedule of heat output was 130-70 °С. The scheme of hot water supply is open.

All the boilers go through inspection on a regular basis. Subject to the results of inspection permission for their operation for specified period is issued. After expiration of this period, inspection is renewed and operation term is prolonged. In the table below the fuel consumption data are provided.

Table А 1. Data for coal consumption at KSPU

| Item/year | 2007 | 2008 | 2009 | 2010 |
| --- | --- | --- | --- | --- |
| Coal consumption at KSPU (tce) | 55 196 | 76 742 | 100 098 | 105 909 |

Electrical boiler-house "Novo-Lenino" (Novo-Lenino EBH) – one of the basic heat supply sources of Novo-Lenino communal sector. The total heat capacity is 156,5 Gcal/h, available heat capacity is 125,0 Gcal/h. The hot water supply capacity is 23 Gcal/h. The temperature schedule of heat output– 130-70 °С, the scheme of hot water supply is open. Installed equipment include electrical boilers KEV-6000/6 (2 units, put into operation in 1981), KEV-8000/6 (2 units, put into operation in 1973, 1986), EVNE-VNE-8000/6 (8 units, put into operation in 1966), KEV-10000/6 (9 units, put into operation in 1981, 1984).

The main parameters of the work of boiler house in 2005-2007 are presented in table А-1.

Electrical boiler-house "Bytovaya" (Bytovaya EBH) also supplies with heat the consumers of Novo-Lenino district. The total heat capacity is 82,6 Gcal/h, available heat capacity is 77,6 Gcal/h. The temperature schedule of heat output is 130-70 °С, the scheme of hot water supply is open, under the closed scheme 43 thermal points at residential buildings in Novo-Lenino district area are connected. Installed equipment include 16 electrical boilers of 3TS-KEV-6000/6 type (launched in 1989, 1998).

The electricity supply of EBHs is carried out from a regional network of JSC “Irkutskenergo” that includes 9 thermal power plants (TPPs) and 3 HPPs (hydro power plants). 80 % of brown coal and 20 % of bituminous coal are used as fuel on TPPs of the Irkutsk power supply system. In the case of reduction in the use of electricity generated at the grid first of all reduction of electricity production at the least efficient condensation cycle occurs. Average specific fuel consumption rate of JSC “Irkutskenergo” for electricity generation under condensation cycle makes 0.399 t.e.c/MWh, the CO2 emission factor makes 1.159 tСО2/MWh. Detailed calculation is presented in Annex 2.